## Commercial 4.4
COMMERCIAL SPRINKLER DATA ENTRY FORM | [11 empty] | SCROLL AND ADD YOUR DATA AT THE BOTTOM OF THE LIST
File | [5 empty] | Static |  | Min Spr Q |  | Min Spr P |  | PIPE DATA |  |  |  | FITTING EQUIVALENT LENGTH
Job | [5 empty] | Resid |  | Density
[6 empty] | Flow |  | Area/Spr |  | Out Hose
[12 empty] | Pipe | Nominal | Actual |  | E | T | L | C | B | G | A | F
NODE | ELEV | KFACT | HOSE | PIPE | B-NOD | E-NOD | LENGTH | DIAM | FITTING | EQLN | C-FACT | Type | Diameter | Diameter | C | 90-E | Tee | LgtElb | ChkVlv | BfyVlv | GatVlv | AlmChk | 45-E
1 |  |  |  | 1 | [7 empty] | Sched-40 | 0.75 | 0.824 | 120 | 2 | 3 | 1 | 0 | 0 | 0 | 0 | 1
2 |  |  |  | 2 | [7 empty] | Sched-40 | 1 | 1.049 | 120 | 2 | 5 | 2 | 5 | 6 | 1 | 10 | 1
3 |  |  |  | 3 | [7 empty] | Sched-40 | 1.25 | 1.38 | 120 | 3 | 6 | 2 | 7 | 6 | 1 | 10 | 1
4 |  |  |  | 4 | [7 empty] | Sched-40 | 1.5 | 1.61 | 120 | 4 | 8 | 2 | 9 | 6 | 1 | 10 | 2
5 |  |  |  | 5 | [7 empty] | Sched-40 | 2 | 2.067 | 120 | 5 | 10 | 3 | 11 | 6 | 1 | 10 | 2
6 |  |  |  | 6 | [7 empty] | Sched-40 | 2.5 | 2.469 | 120 | 6 | 12 | 4 | 14 | 7 | 1 | 10 | 3
7 |  |  |  | 7 | [7 empty] | Sched-40 | 3 | 3.068 | 120 | 7 | 15 | 5 | 16 | 10 | 1 | 13 | 3
8 |  |  |  | 8 | [7 empty] | Sched-40 | 3.5 | 3.548 | 120 | 8 | 17 | 5 | 19 | 11 | 1 | 14 | 3
9 |  |  |  | 9 | [7 empty] | Sched-40 | 4 | 4.026 | 120 | 10 | 20 | 6 | 22 | 12 | 2 | 20 | 4
10 |  |  |  | 10 | [7 empty] | Sched-40 | 5 | 5.047 | 120 | 12 | 25 | 8 | 27 | 9 | 2 | 21 | 5
11 |  |  |  | 11 | [7 empty] | Sched-40 | 6 | 6.065 | 120 | 14 | 30 | 9 | 32 | 10 | 3 | 28 | 7
12 |  |  |  | 12 | [7 empty] | Sched-40 | 8 | 8.071 | 120 | 18 | 35 | 13 | 45 | 12 | 4 | 35 | 9
13 |  |  |  | 13 | [7 empty] | Sched-40 | 10 | 10.136 | 120 | 22 | 50 | 16 | 55 | 19 | 5 | 40 | 11
14 |  |  |  | 14 | [7 empty] | Sched-40 | 12 | 12.09 | 120 | 27 | 60 | 18 | 65 | 21 | 6 | 49 | 13
15 |  |  |  | 15 | [7 empty] | Sched-40 | 16 | 16.53 | 120 | 35 | 70 | 28 | 86 | 22 | 7 | 63 | 0
16 |  |  |  | 16 | [7 empty] | Sched-40 | 18 | 18.61 | 120 | 39 | 85 | 33 | 98 | 39 | 8 | 70 | 0
17 |  |  |  | 17 | [7 empty] | Sched-10 | 1 | 1.097 | 120 | 2.5 | 6.2 | 2.5 | 6.2 | 7.5 | 1.2 | 12.4 | 1.2
18 |  |  |  | 18 | [7 empty] | Sched-10 | 1.25 | 1.442 | 120 | 3.7 | 7.4 | 2.5 | 8.7 | 7.4 | 1.2 | 12.4 | 1.2
19 |  |  |  | 19 | [7 empty] | Sched-10 | 1.5 | 1.682 | 120 | 4.9 | 9.9 | 2.5 | 11.1 | 7.4 | 1.2 | 12.4 | 2.5
20 |  |  |  | 20 | [7 empty] | Sched-10 | 2 | 2.157 | 120 | 6.2 | 12.3 | 3.7 | 13.5 | 7.4 | 1.2 | 12.3 | 2.5
21 |  |  |  | 21 | [7 empty] | Sched-10 | 2.5 | 2.635 | 120 | 8.2 | 16.5 | 5.5 | 19.2 | 9.6 | 1.4 | 13.7 | 4.1
22 |  |  |  | 22 | [7 empty] | Sched-10 | 3 | 3.26 | 120 | 9.4 | 20.2 | 6.7 | 21.5 | 13.4 | 1.3 | 17.5 | 4
23 |  |  |  | 23 | [7 empty] | Sched-10 | 3.5 | 3.76 | 120 | 10.6 | 22.6 | 6.6 | 25.2 | 14.6 | 1.3 | 18.6 | 4
24 |  |  |  | 24 | [7 empty] | Sched-10 | 4 | 4.26 | 120 | 13.2 | 26.3 | 7.9 | 29 | 15.8 | 2.6 | 26.3 | 5.3
25 |  |  |  | 25 | [7 empty] | Sched-10 | 5 | 5.295 | 120 | 15.2 | 31.6 | 10.1 | 34.1 | 11.4 | 2.5 | 26.5 | 6.3
26 |  |  |  | 26 | [7 empty] | Sched-10 | 6 | 6.357 | 120 | 17.6 | 37.7 | 11.3 | 40.2 | 12.6 | 3.8 | 35.2 | 8.8
27 |  |  |  | 27 | [7 empty] | Sched-10 | 8 | 8.249 | 120 | 20 | 38.9 | 14.5 | 50 | 13.3 | 4.4 | 38.9 | 10
[12 empty] | Sched-10 | 10 | 10.374 | 120 | 24.6 | 56 | 17.9 | 61.6 | 21.3 | 5.6 | 44.8 | 12.3
[12 empty] | Sched-10 | 12 | 12.25 | 120 | 28.8 | 64 | 19.2 | 69.3 | 22.4 | 6.4 | 52.2 | 13.9
[12 empty] | Sched-10 | 16 | 16.53 | 120 | 35 | 70 | 28 | 86 | 22 | 7 | 63 | 0
[12 empty] | Sched-10 | 18 | 18.61 | 120 | 39 | 85 | 33 | 98 | 39 | 8 | 70 | 0
[12 empty] | AlliedXL | 1 | 1.104 | 120 | 3 | 6 | 3 | 6 | 0 | 0 | 0 | 1
[12 empty] | AlliedXL | 1.25 | 1.452 | 120 | 4 | 8 | 3 | 9 | 0 | 0 | 0 | 1
[12 empty] | AlliedXL | 1.5 | 1.687 | 120 | 5 | 10 | 3 | 11 | 0 | 0 | 0 | 3
[12 empty] | AlliedXL | 2 | 2.154 | 120 | 6 | 12 | 4 | 13 | 7 | 1 | 0 | 2
[12 empty] | AlliedXL | 2.5 | 2.581 | 120 | 7 | 15 | 5 | 17 | 9 | 1 | 0 | 4
[12 empty] | AlliedXL | 3 | 3.2 | 120 | 9 | 18 | 6 | 20 | 12 | 1 | 0 | 4
[12 empty] | DynaFlow | 1 | 1.191 | 120 | 4 | 10 | 4 | 10 | 0 | 0 | 10 | 2
[12 empty] | DynaFlow | 1.25 | 1.536 | 120 | 5 | 10 | 3 | 12 | 0 | 0 | 10 | 2
[12 empty] | DynaFlow | 1.5 | 1.728 | 120 | 6 | 12 | 3 | 14 | 0 | 0 | 10 | 3
[12 empty] | DynaFlow | 2 | 2.203 | 120 | 7 | 14 | 4 | 16 | 7 | 1 | 10 | 3
[12 empty] | DynaFlow | 2.5 | 2.703 | 120 | 10 | 20 | 10 | 23 | 11 | 2 | 10 | 5
[12 empty] | DynaFlow | 3 | 3.314 | 120 | 11 | 23 | 8 | 25 | 15 | 2 | 13 | 5
[12 empty] | DynaFlow | 4 | 4.31 | 120 | 15 | 29 | 9 | 32 | 18 | 3 | 0 | 6
[12 empty] | DynaThre | 1 | 1.089 | 120 | 2 | 6 | 2 | 6 | 0 | 0 | 0 | 1
[12 empty] | DynaThre | 1.25 | 1.42 | 120 | 3 | 7 | 2 | 8 | 0 | 0 | 0 | 1
[12 empty] | DynaThre | 1.5 | 1.65 | 120 | 5 | 9 | 2 | 10 | 0 | 0 | 0 | 2
[12 empty] | DynaThre | 2 | 2.115 | 120 | 6 | 11 | 3 | 12 | 0 | 1 | 0 | 2
[12 empty] | DuctIron | 4 | 4.28 | 140 | 13 | 27 | 8 | 29 | 16 | 3 | 0 | 0
[12 empty] | DuctIron | 6 | 6.4 | 140 | 19 | 40 | 12 | 43 | 13 | 4 | 0 | 0
[12 empty] | DuctIron | 8 | 8.51 | 140 | 24 | 47 | 17 | 60 | 16 | 5 | 0 | 0
[12 empty] | DuctIron | 10 | 10.52 | 140 | 29 | 67 | 21 | 73 | 25 | 7 | 0 | 0
[12 empty] | DuctIron | 12 | 12.58 | 140 | 36 | 80 | 24 | 86 | 28 | 8 | 0 | 0
[12 empty] | DuctIron | 16 | 16.72 | 140 | 47 | 93 | 37 | 114 | 29 | 9 | 0 | 0
[12 empty] | DuctIron | 18 | 18.8 | 140 | 52 | 113 | 44 | 130 | 52 | 11 | 0 | 0
[12 empty] | DuctIron | 20 | 20.88 | 140 | 59 | 134 | 43 | 146 | 58 | 13 | 0 | 0
[12 empty] | DuctIron | 25 | 25.04 | 140 | 72 | 160 | 48 | 172 | 69 | 16 | 0 | 0
[12 empty] | BlueBrut | 4 | 4.23 | 150 | 15 | 30 | 9 | 33 | 18 | 3 | 0 | 0
[12 empty] | BlueBrut | 6 | 6.09 | 150 | 21 | 45 | 14 | 48 | 15 | 5 | 0 | 0
[12 empty] | BlueBrut | 8 | 7.98 | 150 | 27 | 53 | 20 | 68 | 18 | 6 | 0 | 0
[12 empty] | BlueBrut | 10 | 9.79 | 150 | 33 | 76 | 24 | 83 | 29 | 8 | 0 | 0
[12 empty] | BlueBrut | 12 | 11.65 | 150 | 41 | 91 | 27 | 98 | 32 | 9 | 0 | 0
[12 empty] | BlazMstr | 0.75 | 0.874 | 150 | 7 | 3 | 1 | 3 | 0 | 0 | 0 | 0
[12 empty] | BlazMstr | 1 | 1.101 | 150 | 7 | 5 | 1 | 4 | 6 | 1 | 10 | 0
[12 empty] | BlazMstr | 1.25 | 1.394 | 150 | 8 | 6 | 2 | 5 | 6 | 2 | 10 | 0
[12 empty] | BlazMstr | 1.5 | 1.598 | 150 | 9 | 8 | 2 | 6 | 6 | 2 | 10 | 0
[12 empty] | BlazMstr | 2 | 2.003 | 150 | 11 | 10 | 2 | 8 | 6 | 2 | 10 | 0
[12 empty] | BlazMstr | 2.5 | 2.423 | 150 | 12 | 12 | 3 | 14 | 7 | 1 | 10 | 0
[12 empty] | PVC 150 | 4 | 4.23 | 150 | 15 | 30 | 9 | 33 | 18 | 3 | 0 | 0
[12 empty] | PVC 150 | 6 | 6.09 | 150 | 21 | 45 | 14 | 48 | 15 | 5 | 0 | 0
[12 empty] | PVC 150 | 8 | 7.98 | 150 | 27 | 53 | 20 | 68 | 18 | 6 | 0 | 0
[12 empty] | PVC 150 | 10 | 9.79 | 150 | 33 | 76 | 24 | 83 | 29 | 8 | 0 | 0
[12 empty] | PVC 150 | 12 | 11.65 | 150 | 41 | 91 | 27 | 98 | 32 | 9 | 0 | 0
[12 empty] | Copper K | 0.75 | 0.745 | 150 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0
[12 empty] | Copper K | 1 | 0.995 | 150 | 2 | 3 | 1 | 3 | 3 | 1 | 5 | 1
[12 empty] | Copper K | 1.25 | 1.245 | 150 | 2 | 3 | 1 | 4 | 3 | 1 | 5 | 1
[12 empty] | Copper K | 1.5 | 1.481 | 150 | 3 | 4 | 1 | 5 | 3 | 1 | 5 | 2
[12 empty] | Copper K | 2 | 1.959 | 150 | 4 | 5 | 2 | 6 | 3 | 1 | 5 | 2
[12 empty] | Copper K | 2.5 | 2.435 | 150 | 4 | 6 | 2 | 7 | 4 | 1 | 5 | 3
[12 empty] | Copper K | 3 | 2.907 | 150 | 5 | 8 | 3 | 8 | 5 | 1 | 7 | 3
[12 empty] | Copper K | 3.5 | 3.385 | 150 | 6 | 9 | 3 | 10 | 6 | 1 | 7 | 4
[12 empty] | Copper K | 4 | 3.857 | 150 | 7 | 11 | 3 | 11 | 6 | 1 | 10 | 4
[12 empty] | Copper K | 5 | 4.805 | 150 | 9 | 13 | 4 | 14 | 5 | 1 | 11 | 5
[12 empty] | Copper K | 6 | 5.741 | 150 | 10 | 15 | 5 | 16 | 5 | 2 | 14 | 6
[12 empty] | Copper K | 8 | 7.583 | 150 | 9 | 18 | 7 | 23 | 6 | 2 | 18 | 0
[12 empty] | Copper K | 10 | 9.449 | 150 | 11 | 25 | 8 | 28 | 10 | 3 | 20 | 0
[12 empty] | Copper K | 12 | 11.351 | 150 | 14 | 30 | 9 | 33 | 11 | 3 | 25 | 0
[12 empty] | Copper L | 0.75 | 0.785 | 150 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0
[12 empty] | Copper L | 1 | 1.025 | 150 | 2 | 3 | 1 | 3 | 3 | 1 | 5 | 1
[12 empty] | Copper L | 1.25 | 1.265 | 150 | 2 | 3 | 1 | 4 | 3 | 1 | 5 | 1
[12 empty] | Copper L | 1.5 | 1.505 | 150 | 3 | 4 | 1 | 5 | 3 | 1 | 5 | 2
[12 empty] | Copper L | 2 | 1.985 | 150 | 4 | 5 | 2 | 6 | 3 | 1 | 5 | 2
[12 empty] | Copper L | 2.5 | 2.465 | 150 | 4 | 6 | 2 | 7 | 4 | 1 | 5 | 3
[12 empty] | Copper L | 3 | 2.945 | 150 | 5 | 8 | 3 | 8 | 5 | 1 | 7 | 3
[12 empty] | Copper L | 3.5 | 3.425 | 150 | 6 | 9 | 3 | 10 | 6 | 1 | 7 | 4
[12 empty] | Copper L | 4 | 3.905 | 150 | 7 | 11 | 3 | 11 | 6 | 1 | 10 | 4
[12 empty] | Copper L | 5 | 4.875 | 150 | 9 | 13 | 4 | 14 | 5 | 1 | 11 | 5
[12 empty] | Copper L | 6 | 5.845 | 150 | 10 | 15 | 5 | 16 | 5 | 2 | 14 | 6
[12 empty] | Copper L | 8 | 7.725 | 150 | 9 | 18 | 7 | 23 | 6 | 2 | 18 | 0
[12 empty] | Copper L | 10 | 9.625 | 150 | 11 | 25 | 8 | 28 | 10 | 3 | 20 | 0
[12 empty] | Copper L | 12 | 11.565 | 150 | 14 | 30 | 9 | 33 | 11 | 3 | 25 | 0
[12 empty] | Copper M | 0.75 | 0.811 | 150 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0
[12 empty] | Copper M | 1 | 1.055 | 150 | 2 | 3 | 1 | 3 | 3 | 1 | 5 | 1
[12 empty] | Copper M | 1.25 | 1.291 | 150 | 2 | 3 | 1 | 4 | 3 | 1 | 5 | 1
[12 empty] | Copper M | 1.5 | 1.527 | 150 | 3 | 4 | 1 | 5 | 3 | 1 | 5 | 2
[12 empty] | Copper M | 2 | 2.009 | 150 | 4 | 5 | 2 | 6 | 3 | 1 | 5 | 2
[12 empty] | Copper M | 2.5 | 2.495 | 150 | 4 | 6 | 2 | 7 | 4 | 1 | 5 | 3
[12 empty] | Copper M | 3 | 2.981 | 150 | 5 | 8 | 3 | 8 | 5 | 1 | 7 | 3
[12 empty] | Copper M | 3.5 | 3.459 | 150 | 6 | 9 | 3 | 10 | 6 | 1 | 7 | 4
[12 empty] | Copper M | 4 | 3.935 | 150 | 7 | 11 | 3 | 11 | 6 | 1 | 10 | 4
[12 empty] | Copper M | 5 | 4.907 | 150 | 9 | 13 | 4 | 14 | 5 | 1 | 11 | 5
[12 empty] | Copper M | 6 | 5.881 | 150 | 10 | 15 | 5 | 16 | 5 | 2 | 14 | 6
[12 empty] | Copper M | 8 | 7.785 | 150 | 9 | 18 | 7 | 23 | 6 | 2 | 18 | 0
[12 empty] | Copper M | 10 | 9.701 | 150 | 11 | 25 | 8 | 28 | 10 | 3 | 20 | 0
[12 empty] | Copper M | 12 | 11.617 | 150 | 14 | 30 | 9 | 33 | 11 | 3 | 25 | 0
[12 empty] | Copper D | 1.25 | 1.295 | 150 | 2 | 3 | 1 | 4 | 3 | 1 | 5 | 1
[12 empty] | Copper D | 1.5 | 1.541 | 150 | 3 | 4 | 1 | 5 | 3 | 1 | 5 | 2
[12 empty] | Copper D | 2 | 2.041 | 150 | 4 | 5 | 2 | 6 | 3 | 1 | 5 | 2
[12 empty] | Copper D | 3 | 3.03 | 150 | 5 | 8 | 3 | 8 | 5 | 1 | 7 | 3
[12 empty] | Copper D | 4 | 4.009 | 150 | 7 | 11 | 3 | 11 | 6 | 1 | 10 | 4
[12 empty] | Copper D | 5 | 4.981 | 150 | 9 | 13 | 4 | 14 | 5 | 1 | 11 | 5
[12 empty] | Copper D | 6 | 5.959 | 150 | 10 | 15 | 5 | 16 | 5 | 2 | 14 | 6
[12 empty] | Copper D | 8 | 7.907 | 150 | 9 | 18 | 7 | 23 | 6 | 2 | 18 | 0
[12 empty] | Pipe | Nominal | Actual |  | E | T | L | C | B | G | A | F
[12 empty] | Type | Diameter | Diameter | C | 90-E | Tee | LgtElb | ChkVlv | BfyVlv | GatVlv | AlmChk | 45-E

## Residential 4.4
RESIDENTIAL SPRINKLER DATA ENTRY FORM | [11 empty] | SCROLL AND ADD YOUR PIPE DATA AT THE BOTTOM OF THE LIST
File | [5 empty] | Static |  | Min Spr Q |  | Density
Job | [5 empty] | Resid |  | Area/Spr |  | Meter
[6 empty] | Flow |  | Min Spr P |  | Spr Model |  | PIPE DATA |  |  |  | FITTING EQUIVALENT LENGTH
Spr Mnf
[12 empty] | Pipe | Nominal | Actual |  | E | L | B | R | C | S | G
NODE | ELEV | KFACT | DOM | PIPE | B-NOD | E-NOD | LENGTH | DIAM | FITTING | EQLN | C-FACT | Type | Diameter | Diameter | C | 45-Elb | 90-Elb | TeeBch | TeeRun | CouPlg | SwgChk | GatVlv
1 |  |  |  | 1 | [6 empty] | 150 | BlazMstr | 0.75 | 0.874 | 150 | 1 | 7 | 3 | 1 | 1 | 5 | 1
2 |  |  |  | 2 | [6 empty] | 150 | BlazMstr | 1 | 1.101 | 150 | 1 | 7 | 5 | 1 | 1 | 7 | 1
3 |  |  |  | 3 | [6 empty] | 150 | BlazMstr | 1.25 | 1.394 | 150 | 2 | 8 | 6 | 1 | 1 | 10 | 2
4 |  |  |  | 4 | [6 empty] | 150 | BlazMstr | 1.5 | 1.598 | 150 | 2 | 9 | 8 | 1 | 1 | 13 | 2
5 |  |  |  | 5 | [6 empty] | 150 | BlazMstr | 2 | 2.003 | 150 | 2 | 11 | 10 | 1 | 1 | 17 | 2
6 |  |  |  | 6 | [6 empty] | 150 | BlazMstr | 2.5 | 2.423 | 150 | 3 | 12 | 12 | 2 | 2 | 21 | 2
7 |  |  |  | 7 | [6 empty] | 150 | BlazMstr | 3 | 2.951 | 150 | 4 | 13 | 15 | 2 | 2 | 24 | 2
8 |  |  |  | 8 | [6 empty] | 120 | Copper-M | 0.75 | 0.811 | 150 | 1 | 1 | 2 | 1 | 1 | 5 | 1
9 |  |  |  | 9 | [7 empty] | Copper-M | 1 | 1.055 | 150 | 1 | 2 | 2 | 1 | 1 | 7 | 1
10 |  |  |  | 10 | [7 empty] | Copper-M | 1.25 | 1.291 | 150 | 1 | 2 | 3 | 1 | 1 | 10 | 1
11 |  |  |  | 11 | [7 empty] | Copper-M | 1.5 | 1.527 | 150 | 2 | 3 | 4 | 1 | 1 | 13 | 1
12 |  |  |  | 12 | [7 empty] | Copper-M | 2 | 2.009 | 150 | 2 | 4 | 5 | 1 | 1 | 17 | 1
13 |  |  |  | 13 | [7 empty] | Copper-M | 2.5 | 2.495 | 150 | 3 | 4 | 6 | 2 | 2 | 19 | 1
14 |  |  |  | 14 | [7 empty] | Copper-M | 3 | 2.981 | 150 | 3 | 5 | 8 | 2 | 2 | 21 | 1
15 |  |  |  | 15 | [7 empty] | Copper-M | 4 | 3.935 | 150 | 4 | 7 | 11 | 2 | 2 | 29 | 2
16 |  |  |  | 16 | [7 empty] | Sched-40 | 0.75 | 0.824 | 120 | 1 | 2 | 4 | 1 | 1 | 3 | 1
17 |  |  |  | 17 | [7 empty] | Sched-40 | 1 | 1.049 | 120 | 2 | 2 | 5 | 2 | 2 | 4 | 1
18 |  |  |  | 18 | [7 empty] | Sched-40 | 1.25 | 1.38 | 120 | 2 | 3 | 6 | 2 | 2 | 5 | 2
19 |  |  |  | 19 | [7 empty] | Sched-40 | 1.5 | 1.61 | 120 | 2 | 4 | 8 | 3 | 3 | 6 | 2
20 |  |  |  | 20 | [7 empty] | Sched-40 | 2 | 2.067 | 120 | 3 | 5 | 10 | 3 | 3 | 8 | 2
[12 empty] | Sched-40 | 2.5 | 2.469 | 120 | 3 | 6 | 12 | 4 | 4 | 14 | 2
[12 empty] | Sched-40 | 3 | 3.068 | 120 | 3 | 7 | 15 | 3 | 3 | 16 | 3
[12 empty] | Sched-40 | 3.5 | 3.548 | 120 | 5 | 8 | 17 | 0 | 0 | 19 | 1
[12 empty] | Sched-40 | 4 | 4.026 | 120 | 4 | 10 | 20 | 4 | 4 | 22 | 4
[12 empty] | Sched-40 | 5 | 5.047 | 120 | 8 | 12 | 25 | 0 | 0 | 27 | 2
[12 empty] | Sched-40 | 6 | 6.065 | 120 | 7 | 14 | 30 | 6 | 6 | 32 | 6
[12 empty] | Sched-10 | 1 | 1.097 | 120 | 2.5 | 2.5 | 6.2 | 2.5 | 2.5 | 5 | 1.2
[12 empty] | Sched-10 | 1.25 | 1.442 | 120 | 2.5 | 3.7 | 7.4 | 2.5 | 2.5 | 6.2 | 2.5
[12 empty] | Sched-10 | 1.5 | 1.682 | 120 | 2.5 | 4.9 | 9.9 | 3.7 | 3.7 | 7.4 | 2.5
[12 empty] | Sched-10 | 1 | 2.157 | 120 | 3.7 | 6.2 | 12.3 | 3.7 | 3.7 | 9.8 | 2.5
[12 empty] | Sched-10 | 2.5 | 2.635 | 120 | 4.1 | 8.2 | 16.5 | 5.5 | 5.5 | 19.2 | 2.7
[12 empty] | Sched-10 | 3 | 3.26 | 120 | 4 | 9.4 | 20.2 | 4 | 4 | 21.5 | 4
[12 empty] | Sched-10 | 3.5 | 3.76 | 120 | 6.6 | 10.6 | 22.6 | 0 | 0 | 25.2 | 1.3
[12 empty] | Sched-10 | 4 | 4.26 | 120 | 5.3 | 13.2 | 26.3 | 5.3 | 5.3 | 29 | 5.3
[12 empty] | Sched-10 | 5 | 5.295 | 120 | 10.1 | 15.2 | 31.6 | 0 | 0 | 34.1 | 2.5
[12 empty] | Sched-10 | 6 | 6.357 | 120 | 8.8 | 17.6 | 37.7 | 7.5 | 7.5 | 40.2 | 7.5
[12 empty] | DynaFlow | 1 | 1.191 | 120 | 2 | 2 | 5 | 2 | 2 | 4 | 1
[12 empty] | DynaFlow | 1.25 | 1.536 | 120 | 2 | 3 | 6 | 2 | 2 | 5 | 2
[12 empty] | DynaFlow | 1.5 | 1.728 | 120 | 2 | 4 | 8 | 3 | 3 | 6 | 2
[12 empty] | DynaFlow | 2 | 2.203 | 120 | 3 | 5 | 10 | 3 | 3 | 8 | 2
[12 empty] | DynaFlow | 2.5 | 2.703 | 120 | 3 | 6 | 12 | 4 | 4 | 14 | 2
[12 empty] | DynaFlow | 3 | 3.314 | 120 | 3 | 7 | 15 | 3 | 3 | 16 | 3
[12 empty] | AlliedXL | 1 | 1.104 | 120 | 2 | 2 | 5 | 2 | 2 | 4 | 1
[12 empty] | AlliedXL | 1.25 | 1.452 | 120 | 2 | 3 | 6 | 2 | 2 | 5 | 2
[12 empty] | AlliedXL | 1.5 | 1.687 | 120 | 2 | 4 | 8 | 3 | 3 | 6 | 2
[12 empty] | AlliedXL | 2 | 2.154 | 120 | 3 | 5 | 10 | 3 | 3 | 8 | 2
[12 empty] | AlliedXL | 2.5 | 2.581 | 120 | 3 | 6 | 12 | 4 | 4 | 14 | 2
[12 empty] | AlliedXL | 3 | 3.2 | 120 | 3 | 7 | 15 | 3 | 3 | 16 | 3
[12 empty] | DuctIron | 4 | 4.28 | 140 | 8 | 13 | 27 | 0 | 0 | 29 | 3
[12 empty] | DuctIron | 6 | 6.4 | 140 | 12 | 19 | 40 | 0 | 0 | 43 | 4
[12 empty] | DuctIron | 8 | 8.51 | 140 | 17 | 24 | 47 | 0 | 0 | 60 | 5
[12 empty] | DuctIron | 10 | 10.52 | 140 | 21 | 29 | 67 | 0 | 0 | 73 | 7
[12 empty] | DuctIron | 12 | 12.58 | 140 | 24 | 36 | 80 | 0 | 0 | 86 | 8
[12 empty] | DuctIron | 16 | 16.72 | 140 | 37 | 47 | 93 | 0 | 0 | 114 | 9
[12 empty] | DuctIron | 18 | 18.8 | 140 | 44 | 52 | 113 | 0 | 0 | 130 | 11
[12 empty] | DuctIron | 20 | 20.88 | 140 | 43 | 59 | 134 | 0 | 0 | 146 | 13
[12 empty] | DuctIron | 25 | 25.04 | 140 | 48 | 72 | 160 | 0 | 0 | 172 | 16
[12 empty] | BlueBrut | 4 | 4.23 | 150 | 9 | 15 | 30 | 0 | 0 | 33 | 3
[12 empty] | BlueBrut | 6 | 6.09 | 150 | 14 | 21 | 45 | 0 | 0 | 48 | 5
[12 empty] | BlueBrut | 8 | 7.98 | 150 | 20 | 27 | 53 | 0 | 0 | 68 | 6
[12 empty] | BlueBrut | 10 | 9.79 | 150 | 24 | 33 | 76 | 0 | 0 | 83 | 8
[12 empty] | BlueBrut | 12 | 11.65 | 150 | 27 | 41 | 91 | 0 | 0 | 98 | 9
[12 empty] | Pipe | Nominal | Actual |  | E | L | B | R | C | S | G
[12 empty] | Type | Diameter | Diameter | C | 45-Elb | 90-Elb | TeeBch | TeeRun | CouPlg | SwgChk | GatVlv

## StandPipe 4.32
STANDPIPE DATA ENTRY FORM | [11 empty] | SCROLL AND ADD YOUR PIPE DATA AT THE BOTTOM OF THE LIST
File | [5 empty] | Static |  | SP Min Q |  | SP Min P |  | PIPE DATA |  |  |  | FITTING EQUIVALENT LENGTH
Job | [5 empty] | Resid |  | SP Class
Flow
[12 empty] | Pipe | Nominal | Actual |  | E | T | L | C | B | G | A | F
NODE | ELEV | STP Q | ADD Q | PIPE | B-NOD | E-NOD | LENGTH | DIAM | FITTING | EQLN | C-FACT | Type | Diam | Diam | C | 90-E | Tee | LgtElb | ChkVlv | BfyVlv | GatVlv | AlmChk | 45-E
1 |  |  |  | 1 | [7 empty] | Sched-40 | 0.75 | 0.824 | 120 | 2 | 3 | 1 | 0 | 0 | 0 | 0 | 1
2 |  |  |  | 2 | [7 empty] | Sched-40 | 1 | 1.049 | 120 | 2 | 5 | 2 | 5 | 6 | 1 | 10 | 1
3 |  |  |  | 3 | [7 empty] | Sched-40 | 1.25 | 1.38 | 120 | 3 | 6 | 2 | 7 | 6 | 1 | 10 | 1
4 |  |  |  | 4 | [7 empty] | Sched-40 | 1.5 | 1.61 | 120 | 4 | 8 | 2 | 9 | 6 | 1 | 10 | 2
5 |  |  |  | 5 | [7 empty] | Sched-40 | 2 | 2.067 | 120 | 5 | 10 | 3 | 11 | 6 | 1 | 10 | 2
6 |  |  |  | 6 | [7 empty] | Sched-40 | 2.5 | 2.469 | 120 | 6 | 12 | 4 | 14 | 7 | 1 | 10 | 3
7 |  |  |  | 7 | [7 empty] | Sched-40 | 3 | 3.068 | 120 | 7 | 15 | 5 | 16 | 10 | 1 | 13 | 3
8 |  |  |  | 8 | [7 empty] | Sched-40 | 3.5 | 3.548 | 120 | 8 | 17 | 5 | 19 | 11 | 1 | 14 | 3
9 |  |  |  | 9 | [7 empty] | Sched-40 | 4 | 4.026 | 120 | 10 | 20 | 6 | 22 | 12 | 2 | 20 | 4
10 |  |  |  | 10 | [7 empty] | Sched-40 | 5 | 5.047 | 120 | 12 | 25 | 8 | 27 | 9 | 2 | 21 | 5
11 |  |  |  | 11 | [7 empty] | Sched-40 | 6 | 6.065 | 120 | 14 | 30 | 9 | 32 | 10 | 3 | 28 | 7
12 |  |  |  | 12 | [7 empty] | Sched-40 | 8 | 8.071 | 120 | 18 | 35 | 13 | 45 | 12 | 4 | 35 | 9
13 |  |  |  | 13 | [7 empty] | Sched-40 | 10 | 10.136 | 120 | 22 | 50 | 16 | 55 | 19 | 5 | 40 | 11
14 |  |  |  | 14 | [7 empty] | Sched-40 | 12 | 12.09 | 120 | 27 | 60 | 18 | 65 | 21 | 6 | 49 | 13
15 |  |  |  | 15 | [7 empty] | Sched-40 | 16 | 16.53 | 120 | 35 | 70 | 28 | 86 | 22 | 7 | 63 | 0
16 |  |  |  | 16 | [7 empty] | Sched-40 | 18 | 18.61 | 120 | 39 | 85 | 33 | 98 | 39 | 8 | 70 | 0
17 |  |  |  | 17 | [7 empty] | Sched-10 | 1 | 1.097 | 120 | 2.5 | 6.2 | 2.5 | 6.2 | 7.5 | 1.2 | 12.4 | 1.2
18 |  |  |  | 18 | [7 empty] | Sched-10 | 1.25 | 1.442 | 120 | 3.7 | 7.4 | 2.5 | 8.7 | 7.4 | 1.2 | 12.4 | 1.2
19 |  |  |  | 19 | [7 empty] | Sched-10 | 1.5 | 1.682 | 120 | 4.9 | 9.9 | 2.5 | 11.1 | 7.4 | 1.2 | 12.4 | 2.5
20 |  |  |  | 20 | [7 empty] | Sched-10 | 2 | 2.157 | 120 | 6.2 | 12.3 | 3.7 | 13.5 | 7.4 | 1.2 | 12.3 | 2.5
21 |  |  |  | 21 | [7 empty] | Sched-10 | 2.5 | 2.635 | 120 | 8.2 | 16.5 | 5.5 | 19.2 | 9.6 | 1.4 | 13.7 | 4.1
22 |  |  |  | 22 | [7 empty] | Sched-10 | 3 | 3.26 | 120 | 9.4 | 20.2 | 6.7 | 21.5 | 13.4 | 1.3 | 17.5 | 4
23 |  |  |  | 23 | [7 empty] | Sched-10 | 3.5 | 3.76 | 120 | 10.6 | 22.6 | 6.6 | 25.2 | 14.6 | 1.3 | 18.6 | 4
24 |  |  |  | 24 | [7 empty] | Sched-10 | 4 | 4.26 | 120 | 13.2 | 26.3 | 7.9 | 29 | 15.8 | 2.6 | 26.3 | 5.3
25 |  |  |  | 25 | [7 empty] | Sched-10 | 5 | 5.295 | 120 | 15.2 | 31.6 | 10.1 | 34.1 | 11.4 | 2.5 | 26.5 | 6.3
26 |  |  |  | 26 | [7 empty] | Sched-10 | 6 | 6.357 | 120 | 17.6 | 37.7 | 11.3 | 40.2 | 12.6 | 3.8 | 35.2 | 8.8
27 |  |  |  | 27 | [7 empty] | Sched-10 | 8 | 8.249 | 120 | 20 | 38.9 | 14.5 | 50 | 13.3 | 4.4 | 38.9 | 10
[12 empty] | Sched-10 | 10 | 10.374 | 120 | 24.6 | 56 | 17.9 | 61.6 | 21.3 | 5.6 | 44.8 | 12.3
[12 empty] | Sched-10 | 12 | 12.25 | 120 | 28.8 | 64 | 19.2 | 69.3 | 22.4 | 6.4 | 52.2 | 13.9
[12 empty] | Sched-10 | 16 | 16.53 | 120 | 35 | 70 | 28 | 86 | 22 | 7 | 63 | 0
[12 empty] | Sched-10 | 18 | 18.61 | 120 | 39 | 85 | 33 | 98 | 39 | 8 | 70 | 0
[12 empty] | AlliedXL | 1 | 1.104 | 120 | 3 | 6 | 3 | 6 | 0 | 0 | 0 | 1
[12 empty] | AlliedXL | 1.25 | 1.452 | 120 | 4 | 8 | 3 | 9 | 0 | 0 | 0 | 1
[12 empty] | AlliedXL | 1.5 | 1.687 | 120 | 5 | 10 | 3 | 11 | 0 | 0 | 0 | 3
[12 empty] | AlliedXL | 2 | 2.154 | 120 | 6 | 12 | 4 | 13 | 7 | 1 | 0 | 2
[12 empty] | AlliedXL | 2.5 | 2.581 | 120 | 7 | 15 | 5 | 17 | 9 | 1 | 0 | 4
[12 empty] | AlliedXL | 3 | 3.2 | 120 | 9 | 18 | 6 | 20 | 12 | 1 | 0 | 4
[12 empty] | DynaFlow | 1 | 1.191 | 120 | 4 | 10 | 4 | 10 | 0 | 0 | 10 | 2
[12 empty] | DynaFlow | 1.25 | 1.536 | 120 | 5 | 10 | 3 | 12 | 0 | 0 | 10 | 2
[12 empty] | DynaFlow | 1.5 | 1.728 | 120 | 6 | 12 | 3 | 14 | 0 | 0 | 10 | 3
[12 empty] | DynaFlow | 2 | 2.203 | 120 | 7 | 14 | 4 | 16 | 7 | 1 | 10 | 3
[12 empty] | DynaFlow | 2.5 | 2.703 | 120 | 10 | 20 | 10 | 23 | 11 | 2 | 10 | 5
[12 empty] | DynaFlow | 3 | 3.314 | 120 | 11 | 23 | 8 | 25 | 15 | 2 | 13 | 5
[12 empty] | DynaFlow | 4 | 4.31 | 120 | 15 | 29 | 9 | 32 | 18 | 3 | 0 | 6
[12 empty] | DynaThre | 1 | 1.089 | 120 | 2 | 6 | 2 | 6 | 0 | 0 | 0 | 1
[12 empty] | DynaThre | 1.25 | 1.42 | 120 | 3 | 7 | 2 | 8 | 0 | 0 | 0 | 1
[12 empty] | DynaThre | 1.5 | 1.65 | 120 | 5 | 9 | 2 | 10 | 0 | 0 | 0 | 2
[12 empty] | DynaThre | 2 | 2.115 | 120 | 6 | 11 | 3 | 12 | 0 | 1 | 0 | 2
[12 empty] | DuctIron | 4 | 4.28 | 140 | 13 | 27 | 8 | 29 | 16 | 3 | 0 | 0
[12 empty] | DuctIron | 6 | 6.4 | 140 | 19 | 40 | 12 | 43 | 13 | 4 | 0 | 0
[12 empty] | DuctIron | 8 | 8.51 | 140 | 24 | 47 | 17 | 60 | 16 | 5 | 0 | 0
[12 empty] | DuctIron | 10 | 10.52 | 140 | 29 | 67 | 21 | 73 | 25 | 7 | 0 | 0
[12 empty] | DuctIron | 12 | 12.58 | 140 | 36 | 80 | 24 | 86 | 28 | 8 | 0 | 0
[12 empty] | DuctIron | 16 | 16.72 | 140 | 47 | 93 | 37 | 114 | 29 | 9 | 0 | 0
[12 empty] | DuctIron | 18 | 18.8 | 140 | 52 | 113 | 44 | 130 | 52 | 11 | 0 | 0
[12 empty] | DuctIron | 20 | 20.88 | 140 | 59 | 134 | 43 | 146 | 58 | 13 | 0 | 0
[12 empty] | DuctIron | 25 | 25.04 | 140 | 72 | 160 | 48 | 172 | 69 | 16 | 0 | 0
[12 empty] | BlueBrut | 4 | 4.23 | 150 | 15 | 30 | 9 | 33 | 18 | 3 | 0 | 0
[12 empty] | BlueBrut | 6 | 6.09 | 150 | 21 | 45 | 14 | 48 | 15 | 5 | 0 | 0
[12 empty] | BlueBrut | 8 | 7.98 | 150 | 27 | 53 | 20 | 68 | 18 | 6 | 0 | 0
[12 empty] | BlueBrut | 10 | 9.79 | 150 | 33 | 76 | 24 | 83 | 29 | 8 | 0 | 0
[12 empty] | BlueBrut | 12 | 11.65 | 150 | 41 | 91 | 27 | 98 | 32 | 9 | 0 | 0
[12 empty] | BlazMstr | 0.75 | 0.874 | 150 | 7 | 3 | 1 | 3 | 0 | 0 | 0 | 0
[12 empty] | BlazMstr | 1 | 1.101 | 150 | 7 | 5 | 1 | 4 | 6 | 1 | 10 | 0
[12 empty] | BlazMstr | 1.25 | 1.394 | 150 | 8 | 6 | 2 | 5 | 6 | 2 | 10 | 0
[12 empty] | BlazMstr | 1.5 | 1.598 | 150 | 9 | 8 | 2 | 6 | 6 | 2 | 10 | 0
[12 empty] | BlazMstr | 2 | 2.003 | 150 | 11 | 10 | 2 | 8 | 6 | 2 | 10 | 0
[12 empty] | BlazMstr | 2.5 | 2.423 | 150 | 12 | 12 | 3 | 14 | 7 | 1 | 10 | 0
[12 empty] | PVC 150 | 4 | 4.23 | 150 | 15 | 30 | 9 | 33 | 18 | 3 | 0 | 0
[12 empty] | PVC 150 | 6 | 6.09 | 150 | 21 | 45 | 14 | 48 | 15 | 5 | 0 | 0
[12 empty] | PVC 150 | 8 | 7.98 | 150 | 27 | 53 | 20 | 68 | 18 | 6 | 0 | 0
[12 empty] | PVC 150 | 10 | 9.79 | 150 | 33 | 76 | 24 | 83 | 29 | 8 | 0 | 0
[12 empty] | PVC 150 | 12 | 11.65 | 150 | 41 | 91 | 27 | 98 | 32 | 9 | 0 | 0
[12 empty] | Copper K | 0.75 | 0.745 | 150 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0
[12 empty] | Copper K | 1 | 0.995 | 150 | 2 | 3 | 1 | 3 | 3 | 1 | 5 | 1
[12 empty] | Copper K | 1.25 | 1.245 | 150 | 2 | 3 | 1 | 4 | 3 | 1 | 5 | 1
[12 empty] | Copper K | 1.5 | 1.481 | 150 | 3 | 4 | 1 | 5 | 3 | 1 | 5 | 2
[12 empty] | Copper K | 2 | 1.959 | 150 | 4 | 5 | 2 | 6 | 3 | 1 | 5 | 2
[12 empty] | Copper K | 2.5 | 2.435 | 150 | 4 | 6 | 2 | 7 | 4 | 1 | 5 | 3
[12 empty] | Copper K | 3 | 2.907 | 150 | 5 | 8 | 3 | 8 | 5 | 1 | 7 | 3
[12 empty] | Copper K | 3.5 | 3.385 | 150 | 6 | 9 | 3 | 10 | 6 | 1 | 7 | 4
[12 empty] | Copper K | 4 | 3.857 | 150 | 7 | 11 | 3 | 11 | 6 | 1 | 10 | 4
[12 empty] | Copper K | 5 | 4.805 | 150 | 9 | 13 | 4 | 14 | 5 | 1 | 11 | 5
[12 empty] | Copper K | 6 | 5.741 | 150 | 10 | 15 | 5 | 16 | 5 | 2 | 14 | 6
[12 empty] | Copper K | 8 | 7.583 | 150 | 9 | 18 | 7 | 23 | 6 | 2 | 18 | 0
[12 empty] | Copper K | 10 | 9.449 | 150 | 11 | 25 | 8 | 28 | 10 | 3 | 20 | 0
[12 empty] | Copper K | 12 | 11.351 | 150 | 14 | 30 | 9 | 33 | 11 | 3 | 25 | 0
[12 empty] | Copper L | 0.75 | 0.785 | 150 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0
[12 empty] | Copper L | 1 | 1.025 | 150 | 2 | 3 | 1 | 3 | 3 | 1 | 5 | 1
[12 empty] | Copper L | 1.25 | 1.265 | 150 | 2 | 3 | 1 | 4 | 3 | 1 | 5 | 1
[12 empty] | Copper L | 1.5 | 1.505 | 150 | 3 | 4 | 1 | 5 | 3 | 1 | 5 | 2
[12 empty] | Copper L | 2 | 1.985 | 150 | 4 | 5 | 2 | 6 | 3 | 1 | 5 | 2
[12 empty] | Copper L | 2.5 | 2.465 | 150 | 4 | 6 | 2 | 7 | 4 | 1 | 5 | 3
[12 empty] | Copper L | 3 | 2.945 | 150 | 5 | 8 | 3 | 8 | 5 | 1 | 7 | 3
[12 empty] | Copper L | 3.5 | 3.425 | 150 | 6 | 9 | 3 | 10 | 6 | 1 | 7 | 4
[12 empty] | Copper L | 4 | 3.905 | 150 | 7 | 11 | 3 | 11 | 6 | 1 | 10 | 4
[12 empty] | Copper L | 5 | 4.875 | 150 | 9 | 13 | 4 | 14 | 5 | 1 | 11 | 5
[12 empty] | Copper L | 6 | 5.845 | 150 | 10 | 15 | 5 | 16 | 5 | 2 | 14 | 6
[12 empty] | Copper L | 8 | 7.725 | 150 | 9 | 18 | 7 | 23 | 6 | 2 | 18 | 0
[12 empty] | Copper L | 10 | 9.625 | 150 | 11 | 25 | 8 | 28 | 10 | 3 | 20 | 0
[12 empty] | Copper L | 12 | 11.565 | 150 | 14 | 30 | 9 | 33 | 11 | 3 | 25 | 0
[12 empty] | Copper M | 0.75 | 0.811 | 150 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0
[12 empty] | Copper M | 1 | 1.055 | 150 | 2 | 3 | 1 | 3 | 3 | 1 | 5 | 1
[12 empty] | Copper M | 1.25 | 1.291 | 150 | 2 | 3 | 1 | 4 | 3 | 1 | 5 | 1
[12 empty] | Copper M | 1.5 | 1.527 | 150 | 3 | 4 | 1 | 5 | 3 | 1 | 5 | 2
[12 empty] | Copper M | 2 | 2.009 | 150 | 4 | 5 | 2 | 6 | 3 | 1 | 5 | 2
[12 empty] | Copper M | 2.5 | 2.495 | 150 | 4 | 6 | 2 | 7 | 4 | 1 | 5 | 3
[12 empty] | Copper M | 3 | 2.981 | 150 | 5 | 8 | 3 | 8 | 5 | 1 | 7 | 3
[12 empty] | Copper M | 3.5 | 3.459 | 150 | 6 | 9 | 3 | 10 | 6 | 1 | 7 | 4
[12 empty] | Copper M | 4 | 3.935 | 150 | 7 | 11 | 3 | 11 | 6 | 1 | 10 | 4
[12 empty] | Copper M | 5 | 4.907 | 150 | 9 | 13 | 4 | 14 | 5 | 1 | 11 | 5
[12 empty] | Copper M | 6 | 5.881 | 150 | 10 | 15 | 5 | 16 | 5 | 2 | 14 | 6
[12 empty] | Copper M | 8 | 7.785 | 150 | 9 | 18 | 7 | 23 | 6 | 2 | 18 | 0
[12 empty] | Copper M | 10 | 9.701 | 150 | 11 | 25 | 8 | 28 | 10 | 3 | 20 | 0
[12 empty] | Copper M | 12 | 11.617 | 150 | 14 | 30 | 9 | 33 | 11 | 3 | 25 | 0
[12 empty] | Copper D | 1.25 | 1.295 | 150 | 2 | 3 | 1 | 4 | 3 | 1 | 5 | 1
[12 empty] | Copper D | 1.5 | 1.541 | 150 | 3 | 4 | 1 | 5 | 3 | 1 | 5 | 2
[12 empty] | Copper D | 2 | 2.041 | 150 | 4 | 5 | 2 | 6 | 3 | 1 | 5 | 2
[12 empty] | Copper D | 3 | 3.03 | 150 | 5 | 8 | 3 | 8 | 5 | 1 | 7 | 3
[12 empty] | Copper D | 4 | 4.009 | 150 | 7 | 11 | 3 | 11 | 6 | 1 | 10 | 4
[12 empty] | Copper D | 5 | 4.981 | 150 | 9 | 13 | 4 | 14 | 5 | 1 | 11 | 5
[12 empty] | Copper D | 6 | 5.959 | 150 | 10 | 15 | 5 | 16 | 5 | 2 | 14 | 6
[12 empty] | Copper D | 8 | 7.907 | 150 | 9 | 18 | 7 | 23 | 6 | 2 | 18 | 0
[12 empty] | Pipe | Nominal | Actual |  | E | T | L | C | B | G | A | F
[12 empty] | Type | Diam | Diam | C | 90-E | Tee | LgtElb | ChkVlv | BfyVlv | GatVlv | AlmChk | 45-E